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 PART 1 - GENERAL
1.1 [bookmark: _GoBack]Section Includes
      Edit acoustical where required



A. Sprayed cellulose Fire [and acoustical] spray material.

1.2 Related Items
A. Inspect all wall assemblies to determine if walls meet the UL 395 specification or any other approved UL assemblies.

1.3 Submittals
A. Submit product data and manufacturer's certificate that the product meets or exceeds specified requirements.
B.	Manufacturer's written certification that product contains no asbestos, fiberglass or other man-made mineral fibers, and free of ammonium based additives.
C.	Copy of manufacturer’s ISO 9001:2008 Certification.

1.4 Quality Assurance
A. Manufacturer must be ISO 9001:2008 Certification.
B. Manufacturer must subscribe to independent laboratory follow-up inspection services of Underwriters Laboratories. Each bag shall be labeled accordingly.

1.5 Delivery, Storage and Handling
A. Deliver in original, unopened containers bearing name of manufacturer, product identification and reference to U.L. testing.
B. Store materials dry, off ground, and under cover.

PART 2 - PRODUCTS
2.1 Acceptable Manufacturers
A. International Cellulose Corporation 12315 Robin Boulevard
Houston, Texas 77045
(713) 433-6701 or (800) 444-1252
FAX:  (713) 433-2029

2.2 Materials
A. Celbar RL
1. The sprayed insulation must have been tested in sprayed form by U.L. and have each bag labeled with the reference to U.L. test results according to ASTM E-84/U.L. 723:
a. Tested at a minimum of 4” thickness, Class 1 (A)
b. Flame Spread: 15
c. Smoke Developed: 0
2. Comply with local Building Code Requirements.
3. Fire Rating: 2 Hour UL 395.

PART 3 - EXECUTION
3.1 Preparation
A. Provide masking, drop cloths or other satisfactory coverings for materials/surfaces that are not to receive insulation to prevent damage from over-spray.
B. Coordinate installation of the sprayed cellulose fiber with work of other trades.
C. Install Celweb as needed. See Tech Bulletin for complete instructions.

3.2 Installation
A. Install spray applied insulation according to manufacturer’s recommendations. Apply material with specially designed nozzle using pressure recommended by the manufacturer.
B. Cure insulation with continuous natural or mechanical ventilation.
C. Remove and dispose of over-spray.

3.3 Protection
A.	Protect finished installation under provisions of Division 1.
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