PART 1 – GENERAL
1.01 Section Includes
A. SonaSpray “fc”® sprayed cellulose acoustical finish system (09 83 16)

1.02 Related Items
A. Clips, hangers, supports, sleeves and other attachments to spray bases are to be placed by other trades prior to the application of sprayed finish.
B. Ducts, piping, conduit or other suspended equipment shall not be positioned until after the application of sprayed finish.
C. Roof penetrations to be installed prior to application.

1.03 Quality Assurance
A. Manufacturer must be in compliance with the 2009-2021 International Building Code.
B. Manufacturer must be ISO 9001:2015 Certified.
C. Manufacturer shall have a minimum 10-year successful performance history of producing and installation of spray-applied cellulose on similar projects
D. Applicator: Licensed by manufacturer.
E. Mock-up: Apply a 100 square foot representative sample to be reviewed by the Architect and/or Owner prior to proceeding.
F. Material must be tested in accordance with ASTM E 1042 by a NVLAP accredited testing laboratory.

1.04 Submittals
A. Submit product data that the product meets or exceeds the following specified requirements.
1. Bond strength shall be greater than 600 psf per ASTM E 736.
2. Product shall be Class 1 Class A per ASTM E 84/ UL 723.
3. Non-corrosive per ASTM C 1149
4. Bond Deflection per ASTM E 759: 6” Deflection in 10’ Span – No Spalling or De- lamination.
5. Comply with 2015 IBC Section 803.12 stability requirements for interior finishes.
6. Product shall be Cradle to Cradle® Certified v.3.1 or higher to a minimum certification level of Bronze
7. Product shall be UL GREENGUARD Gold Certified
8. Product must have a publicly available Health Product Declaration (HPD) to 100 PPM
9. Product must have a third-party verified, publicly available, product-specific Environmental Product Declaration per ISO 14025
10. Manufacturer's written certification that product contains no asbestos, fiberglass or other man-made mineral fibers.
11. Copy of manufacturer’s ISO 9001:2015 Certification.
12. Minimum Fiber Recycled Content to be 75%.
13. Cannot contain any added Urea-Formaldehyde Resins.

1.06 Delivery, Storage and Handling

A. Deliver in original, unopened containers bearing name of manufacturer, product identification and reference to U.L. testing.
B. Store materials dry, off ground, and under cover.
C. Protect liquid adhesive from freezing.
D. Water to be potable.
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2.01 Acceptable Manufacturers
A. International Cellulose Corporation 12315 Robin Boulevard
Houston, Texas 77045
Phone: (713) 433-6701 or (800) 444-1252
Fax: (713) 433-2029
Website: www.spray-on.com Email: icc@saint-gobain.com
B. For approved applicators contact ICC at (800) 444-1252.

2.02 Materials
A. SonaSpray “fc”® Acoustical Finish System
1. Color shall be from Manufacturer’s standard color chart or custom color as noted
2. Each bag must be labeled with appropriate UL classification markings
3. Each drum of adhesive must be labeled “SK-2000 FC adhesive to be used with SonaSpray “fc”

PART 3 – EXECUTION
3.01 Examination
A. Examine surfaces and report unsatisfactory conditions in writing. Do not proceed until unsatisfactory conditions are corrected.
B. Verify surfaces to receive spray-applied finish to determine if priming/sealing is required to insure bonding and/or to prevent discoloration caused by migratory stains.

3.02 Preparation
A. Provide masking, drop cloths or other satisfactory coverings for materials/surfaces that are not to receive spray-applied finish to protect from over-spray.
B. Coordinate installation of the sprayed cellulose fiber with work of other trades.
C. Prime surfaces as required by manufacturer’s instructions or as determined by examination.
D. Prime all gypsum board surfaces with high quality, commercial, gypsum board primer

3.03 Installation
A. Install spray applied finish according to manufacturer’s recommendations.
B. Comply with local Building Code requirements.
C. Install spray-applied finish to achieve an average NRC of 	.
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	SonaSpray “fc” Applied on Solid Backing:

	Thickness:
	NRC:

	0.50”
	0.65

	0.75”
	0.75

	1.00”
	0.85

	SonaSpray “fc” Applied on 1.50” Metal Deck:

	Thickness:
	NRC:

	0.75”
	0.80

	1.00”
	0.95

	SonaSpray “fc” Applied on 3.00” Metal Deck:

	Thickness:
	NRC:

	0.50”
	0.80

	0.75”
	0.90

	1.00”
	0.95


Acoustical testing performed by NVLAP certified testing lab.

D. Cure with continuous natural or mechanical ventilation.
a. Continuous ventilation must be maintained until the material has properly cured
E. Remove and dispose of over-spray.

4.01 Protection
A. Protect finished installation under provision of Division 1.
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